## Sheet1
Sr. No | Name of the feeder | Section | Type of conductor | Size | Rated Current of conductor | Total DTC/HTC on this section | Resistance of the section | Reactance of the section | Length | Total connected load in KVA | Remarks
1 | 11KV Durbhat express Feeder | S01 | XLPE cable | 3 X 300 sqmm | 355 | 3 |  |  | 1.959 | 480 |  |  | verified by AE (O&M)
2 | 11KV Durbhat express Feeder | SO2 | XLPE cable | 3 X 300 sqmm | 355 | 3 |  |  | 1.116 | 560 |  |  | verified by AE (O&M)
3 | 11KV Durbhat express Feeder | SO3 | XLPE cable | 3 X 300 sqmm | 355 | 3 |  |  | 1.231 | 600 |  |  | verified by AE (O&M)
4 | 11KV Durbhat express Feeder | SO4 | XLPE cable | 3 X 300 sqmm | 355 | 0 |  |  | 0 | 0 |  |  | verified by AE (O&M)
5 | 11KV Durbhat express Feeder | SO5 | XLPE cable | 3 X 300 sqmm | 355 | 1 |  |  | 0.33 | 200 |  |  | verified by AE (O&M)
6 | 11KV Durbhat express Feeder | SO6 | XLPE cable | 3 X 300 sqmm | 355 | 2 |  |  | 0.979 | 163 |  |  | verified by AE (O&M)
7 | 11KV Durbhat express Feeder | SO7 | XLPE cable | 3 X 300 sqmm | 355 | 2 |  |  | 0.903 | 300 |  |  | verified by AE (O&M)
8 | 11KV Durbhat express Feeder | SO8 | XLPE cable | 3 X 300 sqmm | 355 | 3 |  |  | 1.208 | 460 |  |  | verified by AE (O&M)
9 | 11KV Durbhat express Feeder | SO9 | XLPE cable | 3 X 300 sqmm | 355 | 5 |  |  | 3.312 | 845 |  |  | verified by AE (O&M)
10 | 11KV Durbhat express Feeder | SO10 | XLPE cable | 3 X 300 sqmm | 355 | 4 |  |  | 0.707 | 1193 |  |  | verified by AE (O&M)
Sr. No | Name of the feeder | Name of the DTC/HTC | DTC/HTC capacity in KVA | Impedence %age Voltage | Resistance of Transformer | Year of manufature | Full load of Primary Current as per name plate | Full load of Secondary Current as per name plate | Make/manufatu re details | Short circuit current at 11KV side | %age peak Loading
1 | 11KV Durbhat express Feeder | Dhumre | 160 | 4.85 |  | 2007 | 8.39 | 213.34 | Stanelec | 172.9897 | 80% | verified by AE (O&M)
2 | 11KV Durbhat express Feeder | Manmohan singh | 100 | 4.8 |  | 2020 | 5.248 | 133.33 | Stanelec | 109.3333 | 60% | verified by AE (O&M)
3 | 11KV Durbhat express Feeder | Perigol | 160 | 4.3 |  | 1991 | 8.39 | 213.34 | KEL | 195.1163 | 80% | verified by AE (O&M)
4 | 11KV Durbhat express Feeder | Venktesh leela | 63 | 4.8 |  | Invisible | 3.3 | 84 | Invisible | 68.75 | 60% | verified by AE (O&M)
5 | 11KV Durbhat express Feeder | Ritesh Developers | 400 | 4.5 |  | 2024 | 21 | 533.34 | Shree datta Electrcal | 466.6667 | 55% | verified by AE (O&M)
6 | 11KV Durbhat express Feeder | Rajendra Talak | 630 | 4.38 |  | 2020 | 33.06 | 840 | Stanelec | 754.7945 | 70% | verified by AE (O&M)
7 | 11KV Durbhat express Feeder | Sneh Mandir | 100 | 4.33 |  | 2021 | 5.248 | 133.33 | Stanelec | 121.2009 | 55% | verified by AE (O&M)
8 | 11KV Durbhat express Feeder | Shashikala Pai | 200 | 4.66 |  | 2023 | 10.49 | 266.68 | Sddhi Vinayak | 225.1073 | 60% | verified by AE (O&M)
9 | 11KV Durbhat express Feeder | Galshire | 160 | 4.3 |  | Invisible | 8.39 | 213.34 | Invisible | 195.1163 | 80% | verified by AE (O&M)
10 | 11KV Durbhat express Feeder | Shantadurga | 200 | 4.66 |  | 2000 | 10.49 | 266.68 | Stanelec | 225.1073 | 55% | verified by AE (O&M)
11 | 11KV Durbhat express Feeder | Sanatan-I | 200 | 4.66 |  | 2009 | 10.49 | 266.68 | Stanelec | 225.1073 | 60% | verified by AE (O&M)
12 | 11KV Durbhat express Feeder | Sanatan-II | 200 | 4.66 |  | 2013 | 10.49 | 266.68 | Stanelec | 225.1073 | 80% | verified by AE (O&M)
13 | 11KV Durbhat express Feeder | Ramnathi | 200 | 4.66 |  | 2005 | 10.49 | 266.68 | Stanelec | 225.1073 | 80% | verified by AE (O&M)
14 | 11KV Durbhat express Feeder | Kapileshwari | 200 | 4.66 |  | 2012 | 10.49 | 266.68 | Stanelec | 225.1073 | 60% | verified by AE (O&M)
15 | 11KV Durbhat express Feeder | Matruchaya | 100 | 4.33 |  | 2003 | 5.248 | 133.33 | Stanelec | 121.2009 | 50% | verified by AE (O&M)
16 | 11KV Durbhat express Feeder | Vamneshwar | 63 | 4.8 |  | 2006 | 3.3 | 84 | Stanelec | 68.75 | 60% | verified by AE (O&M)
17 | 11KV Durbhat express Feeder | Golden Properties | 200 | 4.66 |  | 20115 | 10.49 | 266.68 | invisible | 225.1073 | 55% | verified by AE (O&M)
18 | 11KV Durbhat express Feeder | Ritesh | 100 | 4.33 |  | 2009 | 5.248 | 133.33 | Stanelec | 121.2009 | 55% | verified by AE (O&M)
19 | 11KV Durbhat express Feeder | Paunwada | 100 | 4.33 |  | 2018 | 5.248 | 133.33 | Stanelec | 121.2009 | 60% | verified by AE (O&M)
20 | 11KV Durbhat express Feeder | Mahalaxmi Nagar | 200 | 4.66 |  | 1986-87 | 10.49 | 266.68 | KEL | 225.1073 | 80% | verified by AE (O&M)
21 | 11KV Durbhat express Feeder | Talaulim | 200 | 4.66 |  | 1999 | 10.49 | 266.68 | Stanelec | 225.1073 | 50% | verified by AE (O&M)
22 | 11KV Durbhat express Feeder | Wadi | 200 | 4.66 |  | 2015 | 10.49 | 266.68 | Stanelec | 225.1073 | 55% | verified by AE (O&M)
23 | 11KV Durbhat express Feeder | Londiyar | 200 | 4.66 |  | 2007 | 10.49 | 266.68 | Standard | 225.1073 | 80% | verified by AE (O&M)
24 | 11KV Durbhat express Feeder | Kaswada | 100 | 4.33 |  | 2004 | 5.248 | 133.33 | Stanelec | 121.2009 | 75% | verified by AE (O&M)
25 | 11KV Durbhat express Feeder | Sewerage HTC | 145 | 4.34 |  |  | 8.39 | 213.34 |  | 193.318 | 50% | verified by AE (O&M)
26 | 11KV Durbhat express Feeder | Durbhat | 200 | 4.66 |  | 1991 | 10.49 | 266.68 | KEL | 225.1073 | 80% | verified by AE (O&M)
Sr. No | Name of the feeder | Section | Type of conductor | Size | Rated Current of conductor | Total DTC/HTC on this section | Resistance of the section | Reactance of the section | Length | Total connected load in KVA | Remarks
1 | 11KV KARANZAL FEEDER | S01 | XLPE cable | 3 X 300 sqmm | 355 | 1 |  |  | 0.7 | 100 |  | verified by AE (O&M)
2 | 11KV KARANZAL FEEDER | SO2 | XLPE cable | 3 X 300 sqmm | 355 | 3 |  |  | 1.51 | 400 |  | verified by AE (O&M)
3 | 11KV KARANZAL FEEDER | SO3 | XLPE cable | 3 X 300 sqmm | 355 | 6 |  |  | 2.268 | 783 |  | verified by AE (O&M)
4 | 11KV KARANZAL FEEDER | SO4 | XLPE cable | 3 X 300 sqmm | 355 | 2 |  |  | 0.571 | 300 |  | verified by AE (O&M)
5 | 11KV KARANZAL FEEDER | SO5 | XLPE cable | 3 X 300 sqmm | 355 | 1 |  |  | 0.213 | 200 |  | verified by AE (O&M)
6 | 11KV KARANZAL FEEDER | SO6 | XLPE cable | 3 X 300 sqmm | 355 | 0 |  |  | 0.32 | 0 |  | verified by AE (O&M)
7 | 11KV KARANZAL FEEDER | SO7 | XLPE cable | 3 X 300 sqmm | 355 | 1 |  |  | 0.16 | 100 |  | verified by AE (O&M)
8 | 11KV KARANZAL FEEDER | SO8 | XLPE cable | 3 X 300 sqmm | 355 | 2 |  |  | 0.742 | 400 |  | verified by AE (O&M)
Sr. No | Name of the feeder | Name of the DTC/HTC | DTC/HTC capacity in KVA | Impedence %age Voltage | Resistance of Transformer | Year of manufature | Full load of Primary Current as per name plate | Full load of Secondary Current as per name plate | Make/manufatu re details | Short circuit current at 11KV side | %age peak Loading | Remarks
1 | 11KV KARANZAL FEEDER | Konar Gaunem | 100 | 4.85 |  | 2004 | 5.248 | 133.33 | Stanelec | 108.2062 | 50 | verified by AE (O&M)
2 | 11KV KARANZAL FEEDER | MG School | 100 | 4.8 |  | 2002 | 5.248 | 133.33 | Stanelec | 109.3333 | 55 | verified by AE (O&M)
3 | 11KV KARANZAL FEEDER | Chaferan | 200 | 4.66 |  | 2022 | 10.49 | 266.68 | Stanelec | 225.1073 | 65 | verified by AE (O&M)
4 | 11KV KARANZAL FEEDER | Shigmomand | 100 | 4.8 |  | 2009 | 5.248 | 133.33 | Stanelec | 109.3333 | 70 | verified by AE (O&M)
5 | 11KV KARANZAL FEEDER | Mogru | 160 | 4.85 |  | 2000 | 8.39 | 213.34 | Standard | 172.9897 | 50 | verified by AE (O&M)
6 | 11KV KARANZAL FEEDER | Shamrao Builder | 200 | 4.66 |  | 2024 | 10.49 | 266.68 | Siddhi vinayak | 225.1073 | 60 | verified by AE (O&M)
7 | 11KV KARANZAL FEEDER | Kunal | 100 | 4.8 |  | 2011 | 5.248 | 133.33 | Stanelec | 109.3333 | 55 | verified by AE (O&M)
8 | 11KV KARANZAL FEEDER | pearls | 63 | 4.8 |  | 2001 | 3.3 | 84 | Stanelec | 68.75 | 50 | verified by AE (O&M)
9 | 11KV KARANZAL FEEDER | Mahalaxmi Bandora | 200 | 4.66 |  | 2003 | 10.49 | 266.68 | Stanelec | 225.1073 | 55 | verified by AE (O&M)
10 | 11KV KARANZAL FEEDER | Hindu Jan Jagruti | 200 | 4.66 |  |  | 10.49 | 266.68 | invisible | 225.1073 | 70 | verified by AE (O&M)
11 | 11KV KARANZAL FEEDER | Vagdor | 100 | 4.8 |  | 2011 | 5.248 | 133.33 | Stanelec | 109.3333 | 65 | verified by AE (O&M)
12 | 11KV KARANZAL FEEDER | Nagueshi Temple | 200 | 4.66 |  | 2023 | 10.49 | 266.68 | Stanelec | 225.1073 | 55 | verified by AE (O&M)
13 | 11KV KARANZAL FEEDER | Dhonsh | 200 | 4.66 |  | invisible | 10.49 | 266.68 | invisible | 225.1073 | 70 | verified by AE (O&M)
14 | 11KV KARANZAL FEEDER | Nagueshi Panchayat | 200 | 4.66 |  | 2014 | 10.49 | 266.68 | Stanelec | 225.1073 | 60 | verified by AE (O&M)
15 | 11KV KARANZAL FEEDER | Kashimath Ground | 100 | 4.8 |  | 2014 | 5.248 | 133.33 | Stanelec | 109.3333 | 50 | verified by AE (O&M)
Sr. No | Name of the feeder | Section | Type of conductor | Size | Rated Current of conductor | Total DTC/HTC on this section | Resistance of the section | Reactance of the section | Length | Total connected load in KVA | Remarks
1 | 11KV UNDIR FEEDER | S01 | XLPE cable | 3 X 300 sqmm | 355 | 0 |  |  | 0.59 | 0 |  | verified by AE (O&M)
2 | 11KV UNDIR FEEDER | SO2 | XLPE cable | 3 X 300 sqmm | 355 | 1 |  |  | 2.7 | 200 |  | verified by AE (O&M)
3 | 11KV UNDIR FEEDER | SO3 | XLPE cable | 3 X 300 sqmm | 355 | 6 |  |  | 2.743 | 738 |  | verified by AE (O&M)
4 | 11KV UNDIR FEEDER | SO4 | XLPE cable | 3 X 300 sqmm | 355 | 2 |  |  | 0.886 | 200 |  | verified by AE (O&M)
5 | 11KV UNDIR FEEDER | SO5 | XLPE cable | 3 X 300 sqmm | 355 | 1 |  |  | 0.22 | 100 |  | verified by AE (O&M)
Sr. No | Name of the feeder | Name of the DTC/HTC | DTC/HTC capacity in KVA | Impedence %age Voltage | Resistance of Transformer | Year of manufature | Full load of Primary Current as per name plate | Full load of Secondary Current as per name plate | Make/manufatu re details | Short circuit current at 11KV side | %age peak Loading
1 | 11KV UNDIR FEEDER | Kharwada | 100 | 4.8 |  | 2007 | 5.248 | 133.33 | Stanelec | 109.3333 | 50 | verified by AE (O&M)
2 | 11KV UNDIR FEEDER | Konar Gaunem | 100 | 4.8 |  | invisible | 5.248 | 133.33 | invisible | 109.3333 | 60 | verified by AE (O&M)
3 | 11KV UNDIR FEEDER | Talulem Bandora | 200 | 4.66 |  | 2013 | 10.49 | 266.68 | Stanelec | 225.1073 | 70 | verified by AE (O&M)
4 | 11KV UNDIR FEEDER | Ram Mandir | 100 | 4.8 |  | 2012 | 5.248 | 133.33 | Stanelec | 109.3333 | 60 | verified by AE (O&M)
5 | 11KV UNDIR FEEDER | Dempo HTC | 275 | 4.5 |  |  | 10.49 | 266.68 |  | 233.1111 | 50 | verified by AE (O&M)
6 | 11KV UNDIR FEEDER | R B Engineers | 63 | 4.8 |  | invisible | 3.3 | 84 | invisible | 68.75 | 55 | verified by AE (O&M)
7 | 11KV UNDIR FEEDER | Undir Bhakle | 100 | 4.8 |  | 2016 | 5.248 | 133.33 | Stanelec | 109.3333 | 60 | verified by AE (O&M)
8 | 11KV UNDIR FEEDER | Mulebhat | 100 | 4.8 |  | 2016 | 5.248 | 133.33 | Stanelec | 109.3333 | 65 | verified by AE (O&M)
9 | 11KV UNDIR FEEDER | Maruti Temple | 100 | 4.8 |  | 2002 | 5.248 | 133.33 | Standard | 109.3333 | 55 | verified by AE (O&M)
10 | 11KV UNDIR FEEDER | Chickale | 200 | 4.66 |  | 2007 | 10.49 | 266.68 | Stanelec | 225.1073 | 50 | verified by AE (O&M)
11 | 11KV UNDIR FEEDER | Adpai | 200 | 4.66 |  | 1991 | 10.49 | 266.68 | KEL | 225.1073 | 80 | verified by AE (O&M)