## Sheet 1 - Undir_Feeder_Table
Undir_Feeder_Table
Feeders | DURBHAT FEEDER | [40 empty] | UNDIR FEEDER
DTC Name | Dhumre | Manmohan Singh | Perigol | Venktesh Leela | Ritesh Developers | Rajendra Talak | Sneh Mandir | Shashikala Pai | Galshire | Shantadurga | Sanatan-I | Sanatan-II | Ramnathi | Kapileshwari | Matruchaya | Vamneshwar | Golden Properties | Ritesh | Paunwada | Mahalaxmi Nagar | Talaulim | New Talaulim | Wadi | Londiyar | Kaswada | Sewerage HTC | Durbhat | MG School | Chaferan | Shigmomand | Mogru | Shamrao Builder | Kunal | Pearls | Mahalaxmi Bandora | Agrashala | Hindu Jan Jagruti | Vagdor | Nagueshi Temple | Dhoshi | Kashimath Ground | Kharwada | Konar Gaunem | Talulem Bandora | Ram Mandir | Dempo HTC | R B Engineers | Undir Bhakle | Mulebhat | Maruti Temple | Chickale | Adpai | Kavle math | Old Shantadurga | Ramnathu Devasthan | RPRS School | Raigini | Bandora Panchayat
DTC Capacity[KVA] | 200 | 200 | 400 | 200 | 400 | 630 | 200 | Location Inaccessible | 200 | 400 | Transformer Inaccessible | Transformer Inaccessible | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 100 | 200 | 200 | 200 | Location inaccessible | 200 | 200 | 200 | 200 | 200 | 200 | 200 | Transformer Nameplate Damaged | 200 | 200 | 200 | 200
DTC Serial Number | GP/240295 | GP/240297 | 187 | GP/240296 | 83 | GP/200180 | 1209 |  | 1317 | 138 |  |  | 1201 | GP/240293 | 1324 | 1313 | 1319 | 1202 | 1316 | 1329 | 5516 | 1211 | GP/240288 | 1326 | 1328 | 1320 | 1320 | 1200 | G/220612 | 1205 | 1208 | SVT/TR/325211 | 1203 | 1207 | 1204 | GP/240616 | Damaged Nameplate | 1210 | G2/230920 | 1199 | 1330 | 3394 | 5155 | 1150675 | 1318 |  | 1322 | 1321 | 1327 | 1152 | 1316 | 1315 | GP/240617 |  | GP/240614 | 1151 | GP/240615 | 1206
DTC Location{GMap Link] | https://maps.app.goo.gl/vPSuSDBafRHJhhi57?g_st=ipc | https://maps.app.goo.gl/pKPWYufgWCjxAuK19?g_st=ipc | https://maps.app.goo.gl/CKwc6TeeTuLcHfC38?g_st=ipc | https://maps.app.goo.gl/jFDdUGLzFPnAnKv86?g_st=ipc | https://maps.app.goo.gl/iCCpxAtQBh7tcExo8?g_st=ipc | https://maps.app.goo.gl/kt71jeGHDYZ4XeoN8?g_st=ipc | https://maps.app.goo.gl/eYNdKkvADbkXVgtP7?g_st=ipc | https://maps.app.goo.gl/9PhSkma9ELWDWCHy6?g_st=ipc | https://maps.app.goo.gl/HCy3maG53sEMMgYn8?g_st=ipc | https://maps.app.goo.gl/HYtWrf6BnoBMkLt48?g_st=ipc | https://maps.app.goo.gl/AhkNQCKrSyC1xA977?g_st=ipc | https://maps.app.goo.gl/AhkNQCKrSyC1xA977?g_st=ipc | https://maps.app.goo.gl/es4uFygt4tutD3BM7?g_st=ipc | https://maps.app.goo.gl/eaz9xoqh7ZUP1jU39 | https://maps.app.goo.gl/yk6nMUmzqbjSb3UPA?g_st=ipc | https://maps.app.goo.gl/7HX3no7UCSLNBZt26?g_st=ipc | https://maps.google.com?q=15.3876657,73.9971917&entry=gps&lucs=,94284493,94224825,94227247,94227248,94231188,94280568,47071704,47069508,94218641,94282134,94203019,47084304&g_st=ipc | https://maps.google.com?q=15.3881354,73.9981087&entry=gps&lucs=,94284493,94224825,94227247,94227248,94231188,94280568,47071704,47069508,94218641,94282134,94203019,47084304&g_st=ipc | https://maps.app.goo.gl/WMqVkVn2WFVL5jGX6?g_st=ipc | https://maps.app.goo.gl/zuCerCG8QEM7YdCM8?g_st=ipc | https://maps.app.goo.gl/36uwRKViTDFgydSZA?g_st=ipc | https://maps.app.goo.gl/jcJ4uXBFGaVduCCWA?g_st=ipc | https://maps.app.goo.gl/1cNzU8Ea8mgzN8vu7?g_st=ipc | https://maps.app.goo.gl/i8Defrwpb1jzuWpF9?g_st=ipc | https://maps.google.com?q=15.3746636,73.9758229&entry=gps&lucs=,94284457,94224825,94227247,94227248,94231188,94280564,47071704,47069508,94218641,94282134,94203019,47084304&g_st=ipc | https://maps.app.goo.gl/nmWuyFG4N5uuBkJV6?g_st=ipc | https://maps.app.goo.gl/jRrsAbbdswyUz9Gf8?g_st=ipc | https://maps.app.goo.gl/FrhL3oL7x97U7pLm7?g_st=ipc | https://maps.google.com?q=15.4186450,73.9706884&entry=gps&lucs=,94284457,94224825,94227247,94227248,94231188,94280564,47071704,47069508,94218641,94282134,94203019,47084304&g_st=ipc | https://maps.app.goo.gl/YiceHKcDVgVDiRZ6A?g_st=ipc | https://maps.app.goo.gl/ePfwxU6tmjZyvzzB8?g_st=ipc | https://maps.app.goo.gl/ZRpsCdfWq8im5RgWA?g_st=ipc | https://maps.app.goo.gl/tugEVKXNi4zDNfzi9?g_st=ipc | https://maps.app.goo.gl/2Kxnx16aefQ6kZwG6?g_st=ipc | https://maps.app.goo.gl/2ee6hQcbq9ZYnaTp7?g_st=ipc | https://maps.google.com?q=15.4061627,73.9807893&entry=gps&lucs=,94284493,94224825,94227247,94227248,94231188,94280568,47071704,47069508,94218641,94282134,94203019,47084304&g_st=ipc | https://maps.app.goo.gl/5EGdvA3fBvzKGoiN7?g_st=ipc | https://maps.app.goo.gl/5Tfsnko1oHkfr1Wn7?g_st=ipc | https://maps.app.goo.gl/eF38TK426vY7DoULA?g_st=ipc | https://maps.app.goo.gl/iLMj3kvx5jJhAW9d7?g_st=ipc | https://maps.google.com?q=15.4039472,73.9907074&entry=gps&lucs=,94284493,94224825,94227247,94227248,94231188,94280568,47071704,47069508,94218641,94282134,94203019,47084304&g_st=ipc | https://maps.app.goo.gl/Ap24LXmsMhsnLsbk8?g_st=ipc | https://maps.app.goo.gl/LKGMb4D1FcyiYLUz5?g_st=ipc | https://maps.app.goo.gl/29Y4kRQ2StMEuzbN6?g_st=ipc | https://maps.app.goo.gl/MsWGfTyGuMFKaNZn7?g_st=ipc | https://maps.app.goo.gl/TfTDWN6yjaQ74HeC6?g_st=ipc | https://maps.app.goo.gl/3h8ezeLSEje5rqG4A?g_st=ipc | https://maps.app.goo.gl/wScGyPuNKPZwhHEG7?g_st=ipc | https://maps.app.goo.gl/HPjv7ChpfxRVJaUx5?g_st=ipc | https://maps.google.com?q=15.3828297,73.9631793&entry=gps&lucs=,94284457,94224825,94227247,94227248,94231188,94280564,47071704,47069508,94218641,94282134,94203019,47084304&g_st=ipc | https://maps.app.goo.gl/Z8NwmEdEF9LuJVhN8?g_st=ipc | https://maps.google.com?q=15.3728060,73.9672451&entry=gps&lucs=,94284457,94224825,94227247,94227248,94231188,94280564,47071704,47069508,94218641,94282134,94203019,47084304&g_st=ipc | https://maps.app.goo.gl/AWwPScAEsZBC8SGZ6?g_st=ipc | https://maps.app.goo.gl/HYtWrf6BnoBMkLt48?g_st=ipc | https://maps.app.goo.gl/ZQHT8gYmj7A3Ew2G7?g_st=ipc | https://maps.app.goo.gl/kTovamUtL291Y4C9A?g_st=ipc | https://maps.app.goo.gl/4J1Pi5KJf71Y18AK8?g_st=ipc | https://maps.app.goo.gl/txVQE82mm3asHA7G9?g_st=ipc
Coordinates | 15°23'49.6"N 73°59'39.4"E | 15°24'03.4"N 73°59'35.9"E | 15°24'07.1"N 73°59'36.6"E | 15°24'04.2"N 73°59'31.1"E | 15°24'01.4"N 73°59'30.9"E | 15°24'02.4"N 73°59'28.1"E | 15°24'04.1"N 73°59'22.6"E | 15.39624° N, 73.99077° E | 15°23'48.2"N 73°59'13.7"E | 15.3966091, 73.9858989 | 15.3989736, 73.9826702 | 15.3989736, 73.9826702 | 15.3991524, 73.9819849 | 15.39098° N, 73.99390° E | 15°23'18.9"N 73°59'47.1"E | 15°23'08.9"N 73°59'55.4"E | 15°23'15.6"N 73°59'49.9"E | 15°23'17.3"N 73°59'53.2"E | 15.3908714, 73.9876319 | 15.3888627, 73.9840297 | 15.3819016, 73.9801912 | 15.3802885, 73.9820841 | 15.3744813, 73.9820526 | 15°22'38.8"N 73°58'40.8"E | 15.3746962, 73.9757444 | 15°22'17.1"N 73°58'31.0"E | 15°22'17.2"N 73°58'31.2"E | 15°24'56.7"N 73°57'57.8"E | 15.4190119, 73.9704983 | 15°25'12.7"N 73°57'48.2"E | 15°24'20.2"N 73°58'06.4"E | 15°24'12.8"N 73°58'30.6"E | 15°24'15.1"N 73°58'37.5"E | 15°24'17.1"N 73°58'39.3"E | 15°24'23.8"N 73°58'47.5"E | 15°24'22.2"N 73°58'50.8"E | 15°24'13.7"N 73°58'55.4"E | 15°24'11.3"N 73°58'50.8"E | 15°24'29.1"N 73°59'02.4"E | 15°24'36.9"N 73°59'04.8"E | 15°24'14.2"N 73°59'26.6"E | 15.4058394, 73.9615589 | 15°24'41.2"N 73°57'36.5"E | 15.4005258, 73.9708262 | 15.4050368, 73.9562746 | 15.3988905, 73.9541006 | 15.3959852, 73.9556419 | 15.3945869, 73.9579047 | 15.3899896, 73.9610456 | 15.3828290, 73.9631790 | 15.3780984, 73.9632148 | 15.3727747, 73.9671888 | 15.3943005, 73.9867398 | 15.39642° N, 73.98599° E | 15.3981852, 73.9815624 | 15.3991524, 73.9819849 | 15°24'08.0"N 73°59'10.5"E | 15°24'15.7"N 73°59'03.7"E
CT ratio | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 |  | 400:5 | 400:5 |  |  | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 |  | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 | 400:5 |  | 400:5 | 400:5 | 400:5 | 400:5
Multiplying Factor | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 |  |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80
Meter Number | 641 | 849 | 2141 | 1917 |  |  | 0427/05/17 |  | 1991 | 2089 | 427/05/32 | 427/05/32 | 1953 | 1980 | 1975 | 2044 | 0427/05/21 | 0427/05/18 | 1982 |  |  | 427/05/34 |  | 1994 | 1992 | 1985 | 1985 | 0427/05/09 | 0427/05/10 | 0427/05/01 | 0427/05/02 | No energy meter | 0427/05/08 | 0427/05/12 | 0427/05/04 | 2024 | 427/05/33 | 0427/05/13 | 0427/05/03 | 0427/05/05 | 1929 | 8 | 0427/05/11 | 21 | 1988 |  | 27 | 1993 | 1989 | 1990 | 1987 | 1986 | 0427/05/24 | 427/01/66 | 0427/05/16 | 1978 | 2009 | 0427/05/06
Vector Group | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | DY-11 | Dyn-11 |  | Dyn-11 | Dyn-11 |  |  | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 |  | Dyn11 | Dyn11 | Dy11 | Dyn11 | Dyn11 | Dyn11 | Dyn11 | Dyn11 | Dyn11 | Dy n-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 |  | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dyn-11 | Dy-11 | Dyn11 | Dyn11 |  | Dyn11 | Dyn11 | Dyn11 | Dyn11 | Dyn11 | Dyn11 | Dyn11 |  | Dyn11 | Dyn11 | Dyn11 | Dyn11
HV Voltage[V] | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 |  | 11000 | 11000 |  |  | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 |  | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 |  | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 | 11000 |  | 11000 | 11000 | 11000 | 11000
LV Voltage[V] | 433 | 433 | 433 | 433 | 433 | 433 | 433 |  | 433 | 433 |  |  | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 |  | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 |  | 433 | 433 | 433 | 433 | 433 | 433 | 433 |  | 433 | 433 | 433 | 433
HV Current[A] | 10.5 | 10.497 | 21 | 10.497 | 21 | 33.06 | 10.5 |  | 10.5 | 21 |  |  | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.49 | 10.5 | 10.497 | 10.5 | 10.5 | 10.49 | 10.5 | 10.5 | 10.5 | 10.497 |  | 10.49 | 10.49 | 10.49 | 10.5 | 5.25 | 10.49 | 10.49 | 10.5 |  | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.49 | 10.497 |  | 10.497 | 10.5 | 10.5 | 10.5
LV Current[A] | 266.68 | 266.68 | 533.34 | 266.68 | 533.34 | 840 | 266.68 |  | 266.68 | 533.34 |  |  | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.64 | 266.68 | 266.68 | 266.68 | 266.68 |  | 266.68 | 266.68 | 266.68 | 266.68 | 133.3 | 166.68 | 266.68 | 266.68 |  | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 | 266.68 |  | 266.68 | 266.68 | 266.68 | 266.68
Date | 09-10-25 | 09-10-25 | 09-10-25 | 09-10-25 | 09-10-25 | 09-10-25 | 09-10-25 | 10-10-25 | 09-10-25 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 8-10-25 | 8-10-25 | 8-10-25 | 8-10-25 | 8-10-25 | 24-9-25 | 24-9-25 | 24-9-25 | 24-9-25 | 24-9-25 | 24-9-25 | 24-9-25 | 24-9-25 | 24-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 10-10-25 | 10-10-25 | 10-10-25 | 10-10-25 | 10-10-25 | 10-10-25 | 09-10-25 | 09-10-25 | 09-10-25 | 09-10-25 | 09.10.2025 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 24-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 25-9-25 | 09-10-25 | 09-10-25
Time | 11.46 | 11.53 | 11.58 | 12.05 | 12.12 | 12.19 | 3.24 | 4.1 | 3.15 | 3.1 | 3.21 | 3.21 | 3.23 | 11.57 | 11.36 | 11.44 | 12.09 | 12.23 | 2.52 | 3.02 | 3.17 | 3.19 | 3.27 | 3.35 | 3.43 | 3.5 | 4.17 | 4.02 | 4.1 | 4.16 | 3.56 | 3.49 | 3.44 | 3.41 | 3.33 | 3.28 | 3.52 | 3.55 | 3.42 | 3.46 | 12.28 | 3.51 | 3.57 | 3.42 | 12.28 | 12.23 | 12.15 | 12.08 | 11.59 | 11.54 | 11.45 | 3.56 | 3.07 | 3.1 | 3.3 | 3.35 | 3.3 | 3.36
RMU Serial Number | SAB01230094 | SAB01230095 | SAB01230167 | SAB01230090 | SAB11233353 | 908418 | SAB08232363 |  | SAB01230101 | SAB03241116 | SAB01230098 | SAB08232365 | SAB01230097 | SAB01240056 | SAB01240061 | SAB01240067 | SAB12233548 | SAB12233555 | SAB01230105 | SAB01230103 | SAB01230096 | SAB06241989 | SAB01230083 | SAB01230093 | SAB01230085 | SAB01230176 | SAB01230086 | SAB01230099 | SAB01230109 | SAAB01230100 | SAB01230102 | SAB02240431 | SAB01230107 | SAB11233391 | SAB11233389 | SAB1240063 | SAB03241173 | SAB01230166 | SAB08232185 | SAB02240515 | SAB01240351 | SAB06241988 | SAB01230106 | SAB01230108 | SAB01230094 | SAB01230087 | SAB01230092 | SAB08232362 | SAB01230088 | SAB01230104 | SAB01230177 | SAB01230084 | SAB03240813 | SAB08232364 | MYR0706-01 | SAB03240938 | SAB03240899 | SAB11233392
Total Loss[100%][W] | 2300 | 2300 | 3450 | 2300 | 3450 | 5300 | 2300 |  | 2300 | 3450 |  |  | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 |  | 2300 | 2300 | 2300 | 2300 | 1650 | 2300 | 2300 | 2300 |  | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 | 2300 |  | 2300 | 2300 | 2300 | 2300
Total Loss[50%][W] | 780 | 780 | 1225 | 780 | 1225 | 1860 | 780 |  | 780 | 1225 |  |  | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 750 | 780 | 780 | 780 | 780 | 780 | 780 | 780 | 780 |  | 780 | 780 | 780 | 780 | 475 | 780 | 780 | 780 |  | 780 | 780 | 780 | 780 | 780 | 780 | 780 |  | 780 | 780 | 780 | 780
Copper Loss[Pcu][W] | 2026.6667 | 2026.6667 | 2966.6667 | 2026.6667 | 2966.6667 | 4586.6667 | 2026.6667 | 0 | 2026.6667 | 2966.6667 | 0 | 0 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2066.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 0 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 1566.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 0 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667 | 0 | 2026.6667 | 2026.6667 | 2026.6667 | 2026.6667
% Impedence[Z] | 4.35 | 4.05 | 4.5 | 4.3 | 4.5 | 4.38 | 4.5 |  | 4.5 | 4.5 |  |  | 4.5 | 4.3 | 4.5 | 4.5 | 4.5 | 4.5 | 6.5 | 4.5 | 4.66 | 4.5 | 4.3 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.3 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.27 |  | 4.5 | 4.4 | 4.5 | 4.5 | 4..5 | 4.77 | 4.61 | 4.5 |  | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.31 |  | 4.32 | 4.5 | 4.31 | 4.5
Zbase[Secondary] | 0.93744 | 0.93744 | 0.46872 | 0.93744 | 0.46872 | 0.2976 | 0.93744 | #VALUE! | 0.93744 | 0.46872 | #VALUE! | #VALUE! | 0.93744 | 0.93744 | #REF! | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 1.8749 | 0.93744 | 0.93744 | 0.93744 | #VALUE! | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | #VALUE! | 0.93744 | 0.93744 | 0.93744 | 0.93744
Zbase[Primary] | 605 | 605 | 302.5 | 605 | 302.5 | 192.0635 | 605 | #VALUE! | 605 | 302.5 | #VALUE! | #VALUE! | 605 | 605 | #REF! | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | 605 | #DIV/0! | 605 | 605 | 605 | 605 | 1210 | 605 | 605 | 605 | #VALUE! | 605 | 605 | 605 | 605 | 605 | 605 | 605 | #VALUE! | 605 | 605 | 605 | 605
Zactual[Seconary] | 0.040779 | 0.037967 | 0.021093 | 0.04031 | 0.021093 | 0.013035 | 0.042185 | #VALUE! | 0.042185 | 0.021093 | #VALUE! | #VALUE! | 0.042185 | 0.04031 | #REF! | 0.042185 | 0.042185 | 0.042185 | 0.060934 | 0.042185 | 0.043685 | 0.042185 | 0.04031 | 0.042185 | 0.042185 | 0.042185 | 0.042185 | 0.042185 | 0.04031 | 0.042185 | 0.042185 | 0.042185 | 0.042185 | 0.042185 | 0.042185 | 0.040029 | 0 | 0.042185 | 0.041248 | 0.042185 | 0.042185 | #VALUE! | 0.044716 | 0.043216 | 0.042185 | #VALUE! | 0.042185 | 0.042185 | 0.042185 | 0.042185 | 0.042185 | 0.042185 | 0.040404 | #VALUE! | 0.040498 | 0.042185 | 0.040404 | 0.042185
Zactual[Primary] | 26.3175 | 24.5025 | 13.6125 | 26.015 | 13.6125 | 8.4124 | 27.225 | #VALUE! | 27.225 | 13.6125 | #VALUE! | #VALUE! | 27.225 | 26.015 | #REF! | 27.225 | 27.225 | 27.225 | 39.325 | 27.225 | 28.193 | 27.225 | 26.015 | 27.225 | 27.225 | 27.225 | 27.225 | 27.225 | 26.015 | 27.225 | 27.225 | 27.225 | 27.225 | 27.225 | 27.225 | 25.8335 | #DIV/0! | 27.225 | 26.62 | 27.225 | 27.225 | #VALUE! | 28.8585 | 27.8905 | 27.225 | #VALUE! | 27.225 | 27.225 | 27.225 | 27.225 | 27.225 | 27.225 | 26.0755 | #VALUE! | 26.136 | 27.225 | 26.0755 | 27.225
Resistance_actual[Secondary] | 0.0094991 | 0.0094991 | 0.0034765 | 0.0094991 | 0.0034765 | 0.0021668 | 0.0094991 | #DIV/0! | 0.0094991 | 0.0034765 | #DIV/0! | #DIV/0! | 0.0094991 | 0.0094991 | #REF! | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0096865 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0095019 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | #DIV/0! | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.02939 | 0.024316 | 0.0094991 | 0.0094991 | #DIV/0! | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991 | #DIV/0! | 0.0094991 | 0.0094991 | 0.0094991 | 0.0094991
Reactance_actual[Secondary] | 0.039657 | 0.036759 | 0.020804 | 0.039175 | 0.020804 | 0.012854 | 0.041102 | #VALUE! | 0.041102 | 0.020804 | #VALUE! | #VALUE! | 0.041102 | 0.039175 | #REF! | 0.041102 | 0.041102 | 0.041102 | 0.060189 | 0.041102 | 0.04264 | 0.041102 | 0.039175 | 0.041102 | 0.041102 | 0.041102 | 0.041102 | 0.041058 | 0.039175 | 0.041102 | 0.041102 | 0.041101 | 0.041102 | 0.041102 | 0.041102 | 0.038885 | #DIV/0! | 0.041102 | 0.040139 | 0.041102 | 0.041102 | #VALUE! | 0.037527 | 0.042159 | 0.041102 | #VALUE! | 0.041102 | 0.041102 | 0.041102 | 0.041102 | 0.041102 | 0.041102 | 0.039271 | #VALUE! | 0.039368 | 0.041102 | 0.039271 | 0.041102
Resistance_actual[Primary] | 6.1275 | 6.131 | 2.2424 | 6.131 | 2.2424 | 1.3988 | 6.1275 | #DIV/0! | 6.1275 | 2.2424 | #DIV/0! | #DIV/0! | 6.1275 | 6.1275 | #REF! | 6.1275 | 6.1275 | 6.1275 | 6.1275 | 6.1275 | 6.1392 | 6.1392 | 6.1392 | 6.1392 | 6.1392 | 6.1392 | 6.1392 | 6.2484 | 6.131 | 6.1275 | 6.1275 | 6.1392 | 6.1275 | 6.1275 | 6.1275 | 6.131 | #DIV/0! | 6.1392 | 6.1392 | 6.1392 | 6.1275 | 18.9468 | 6.1392 | 6.1392 | 6.1275 | #DIV/0! | 6.1275 | 6.1275 | 6.1275 | 6.1275 | 6.1275 | 6.1392 | 6.131 | #DIV/0! | 6.131 | 6.1275 | 6.1275 | 6.1275
Reactance_actual[Primary] | 25.5942 | 23.7231 | 13.4265 | 25.2822 | 13.4265 | 8.2953 | 26.5265 | #VALUE! | 26.5265 | 13.4265 | #VALUE! | #VALUE! | 26.5265 | 25.2831 | #REF! | 26.5265 | 26.5265 | 26.5265 | 38.8447 | 26.5265 | 27.5165 | 26.5238 | 25.2802 | 26.5238 | 26.5238 | 26.5238 | 26.5238 | 26.4983 | 25.2822 | 26.5265 | 26.5265 | 26.5238 | 26.5265 | 26.5265 | 26.5265 | 25.0954 | #DIV/0! | 26.5238 | 25.9024 | 26.5238 | 26.5265 | #VALUE! | 28.1979 | 27.2064 | 26.5265 | #VALUE! | 26.5265 | 26.5265 | 26.5265 | 26.5265 | 26.5265 | 26.5238 | 25.3445 | #VALUE! | 25.4067 | 26.5265 | 25.3453 | 26.5265
Vrn[R phase Voltage] | 234.15 | 234 | 236 | 235 | 237 | 234 | 238 |  | 248 | 239.78 |  |  | 244 | 235 | 234 | 235.45 | 236.3 | 233 | 240.33 | 242 | 235 | 246 | 244 | 243 | 243 | 243 | 244 | 248 | 245 | 245 | 237 | Damaged Panel | 236 | 235.47 | 235 | 236 | 240 | 238 | 239 | 239 | 242 | 244 | 243 | 239.43 | 245 |  | 249 | 246 | 247 | 244 | 245 | 242 | 238 | 239 | 244 | 244 | 239 | 244
Vyn[Y phase Voltage] | 234.77 | 233 | 239 | 236 | 237 | 231 | 238 |  | 239 | 239.84 |  |  | 245 | 233 | 233 | 236.45 | 236.6 | 241 | 241 | 241 | 233 | 246 | 244 | 242 | 245 | 242 | 245 | 246 | 247 | 247 | 234 |  | 237 | 233.4 | 236 | 238 | 240 | 239 | 239.37 | 239 | 240 | 245 | 244 | 239.09 | 247 |  | 249.22 | 246 | 246 | 244 | 242 | 243 | 240 | 240 | 245 | 243 | 238 | 241
Vbn[B phase Voltage] | 234.93 | 236 | 237 | 237 | 234 | 240 | 237 |  | 239 | 238.15 |  |  | 243 | 234 | 233 | 235.85 | 236.7 | 236 | 240.1 | 242 | 234 | 248 | 245 | 242 | 246 | 244 | 243 | 247 | 245 | 242 | 237 |  | 233 | 231.8 | 234 | 238 | 241 | 238 | 239.2 | 238 | 242 | 243 | 241 | 240.1 | 247 |  | 249.4 | 248 | 245 | 245 | 241 | 243 | 240 | 239 | 243 | 243 | 240 | 242
Ir[R phase Current] | 1.08 | 0.6 | 37 | 0.33 | 0.5 | 31 | 17 |  | 16 | 0.43 |  |  | 0.64 | 19 | 1.47 | 0.41 | 15.07 | 10.09 | 59 | 58 | 19 | 0.31 | 0.53 | 56 | 0.32 | 58 | 0.64 | 6.77 | 20.1 | 8.37 | 28.9 |  | 73.4 | 2.75 | 51.9 | 0.31 | 18.05 | 0.53 | 42 | 51.5 | 5.01 | 0.64 | 7.78 | 0.3 | 0.61 |  | 0.41 | 0.31 | 48 | 0.53 | 70 | 0.14 | 46.23 | 0.43 | 0.64 | 0.26 | 0.76 | 0.52
Iy[Y phase Current] | 0.93 | 0.5 | 31 | 0.77 | 0.71 | 30 | 19 |  | 14 | 0.4 |  |  | 0.33 | 6 | 1.39 | 0.41 | 15 | 13 | 34 | 50 | 6 | 0.14 | 0.49 | 52 | 0.15 | 63 | 0.33 | 6.08 | 19 | 7.15 | 43.9 |  | 56.8 | 2.04 | 50 | 0.14 | 17.66 | 0.49 | 22 | 29.8 | 7.3 | 0.33 | 5.81 | 0.26 | 0.29 |  | 0.35 | 0.14 | 21 | 0.49 | 67 | 0.09 | 45 | 0.36 | 0.2 | 0.08 | 0.34 | 0.77
Ib[B phase Current] | 0.62 | 0.97 | 30 | 0.6 | 0.66 | 33 | 42 |  | 16 | 0.36 |  |  | 0.2 | 4 | 1.17 | 0.43 | 15.1 | 14.12 | 66 | 68 | 4 | 0.25 | 28 | 61 | 0.27 | 48 | 0.2 | 9.68 | 21.5 | 3.51 | 19.6 |  | 68.6 | 3.2 | 54.3 | 0.25 | 19.75 | 28 | 17 | 55.9 | 2.6 | 0.2 | 5.91 | 0.36 | 0.75 |  | 0.43 | 0.25 | 35 | 28 | 65 | 0.03 | 45 | 0.43 | 0.33 | 0.03 | 0.39 | 0.61
[Reactive Energy Consumed]kVArh | 36.27 | 119.18 | 4.69 | 186.62 | CT not connected | 839.37 | 523.11 |  | 261.14 | 261.7 |  |  | 480.84 | 86.16 | 808.2 | 93.31 | energy meter not present | energy meter not present | 413.41 | 711.53 | energy meter not present | energy meter not present | energy meter not present | 362.54 | 250.1 | 348.82 | 480.84 | CT not connected | CT not connected | CT not connected | 0.19 |  | 0.19 | 0.21 | 0.2 | 0.79 | 1.3 | 0.19 | 4.69 | 86.16 | 161.553 | 480.84 | 247.17 | 36.27 | 127.47 |  | CT not connected | 248.9 | 165.72 | 94.15 | 392.09 | 1.3 | energy meter not present | 261.7 | 480.84 | 133.91 | 124 | energy meter not present
[Real Energy Consumed]kWh | 1302.39 | 1258.7 | 268.51 | 957.44 |  | 1274.33 | 999.256 |  | 4108.9 | 1610.35 |  |  | 2729.87 | 611.81 | 5668.53 | 1785.6 |  |  | 3701.68 | 69.4 |  |  |  | 4595.21 | 1431.44 | 3576.53 | 2729.87 |  |  |  | 2.041 |  | 2.032 | 2.051 | 2.047 | 4.06 | 45.39 | 2.041 | 268.51 | 611.81 | 1187.38 | 2729.87 | 1428.41 | 1302.39 | 1812.6 |  |  | 1430.41 | 2866.67 | 1248.3 | 3524.98 | 45.39 |  | 1610.35 | 2722.78 | 1219.07 | 1314.55
[Apparent Energy Consumed]kVAh | 1304.92 | 1264.33 | 268.87 | 977.67 |  | 1525.93 | 1127.9 |  | 4117.2 | 16353.31 |  |  | 2771.9 | 620.77 | 5754.65 | 1792.08 |  |  | 3728.6 | 714.93 |  |  |  | 4613.31 | 1453.42 | 3597.32 | 2771.9 |  |  |  | 2.05 |  | 2.04 | 2.07 | 2.06 | 4.16 | 45.53 | 2.05 | 268.87 | 620.77 | 1198.32 | 2771.9 | 1449.49 | 1304.92 | 1818.86 |  |  | 1451.49 | 2875.63 | 1251.87 | 3546.72 | 45.53 |  | 1635.31 | 2771.9 | 1226.41 | 1321.99
Real Power[kW] | 1.028 | 0.74 | 0.248 | 0.618 |  | 0.7853 | 1.8024 |  | 0.79 | 0.576 |  |  | 0.682 | 0.184 | 1.16 | 0.3 |  |  | 0.914 | 1.506 |  |  |  | 0.922 | 0.342 | 1.558 | 0.682 |  |  |  | 0.2 |  | 0.2 | 0.2 | 0.2 | 0.184 | 0.158 | 0.2 | 0.248 | 0.184 | 0 | 0.682 | 0.347 | 1.028 | 0.902 |  |  | 0.342 | 0.676 | 0.696 | 1.296 | 0.158 |  | 0.576 | 0.682 | 0.488 | 0.742
Reactive Power[kVAr] | 0.258 | 0.038 | 0.144 | 0.295 |  | 0.146 | 0.466 |  | 0.682 | 0.283 |  |  | 0.248 | 0.078 | 0.358 | 0.35 |  |  | 0.21 | 0.134 |  |  |  | 0.27 | 0.135 | 0.721 | 0.248 |  |  |  | 0.46 |  | 0.774 | 0.45 | 0.46 | 0.078 | 0.084 | 0.46 | 0.144 | 0.078 | 0.214 | 0.248 | 0.138 | 0.258 | 0.264 |  |  | 0.135 | 0.052 | 0.064 | 0.485 | 0.084 |  | 0.283 | 0.736 | 0.108 | 0.349
Apparent Power[kVA] | 1.06 | 0.741 | 0.322 | 0.685 |  | 0.7988 | 1.8625 |  | 1.044 | 0.642 |  |  | 0.726 | 0.2 | 1.214 | 0.27 |  |  | 0.938 | 1.512 |  |  |  | 0.963 | 0.368 | 1.674 | 0.726 |  |  |  | 0.502 |  | 0.8 | 0.51 | 0.502 | 0.2 | 0.133 | 0.502 | 0.322 | 0.2 | 0.364 | 0.726 | 0.371 | 1.06 | 0.94 |  |  | 0.368 | 0.678 | 0.699 | 1.384 | 0.133 |  | 0.642 | 0.276 | 0.5 | 0.82
Frequency[Hz] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Conductor Thickness
%R | 1.0133 | 1.0133 | 0.74167 | 1.0133 | 0.74167 | 0.72804 | 1.0133 | #VALUE! | 1.0133 | 0.74167 | #VALUE! | #VALUE! | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0333 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 0 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.5667 | 1.0133 | 1.0133 | 1.0133 | #VALUE! | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | 1.0133 | #VALUE! | 1.0133 | 1.0133 | 1.0133 | 1.0133
%X | 4.2303 | 3.9212 | 4.4385 | 4.1789 | 4.4385 | 4.3191 | 4.3844 | #VALUE! | 4.3844 | 4.4385 | #VALUE! | #VALUE! | 4.3844 | 4.1789 | 4.3844 | 4.3844 | 4.3844 | 4.3844 | 6.4205 | 4.3844 | 4.5485 | 4.3844 | 4.1789 | 4.3844 | 4.3844 | 4.3844 | 4.3844 | 4.3798 | 4.1789 | 4.3844 | 4.3844 | 4.3844 | 4.3844 | 4.3844 | 4.3844 | 4.148 | 0 | 4.3844 | 4.2817 | 4.3844 | 4.3844 | #VALUE! | 4.6611 | 4.4972 | 4.3844 | #VALUE! | 4.3844 | 4.3844 | 4.3844 | 4.3844 | 4.3844 | 4.3844 | 4.1892 | #VALUE! | 4.1995 | 4.3844 | 4.1892 | 4.3844
Iron Loss | 273.3333 | 273.3333 | 483.3333 | 273.3333 | 483.3333 | 713.3333 | 273.3333 | 0 | 273.3333 | 483.3333 | 0 | 0 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 233.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 0 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 83.3333 | 273.3333 | 273.3333 | 273.3333 | 0 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 273.3333 | 0 | 273.3333 | 273.3333 | 273.3333 | 273.3333
%No Load Loss | 0.13667 | 0.13667 | 0.12083 | 0.13667 | 0.12083 | 0.11323 | 0.13667 | #VALUE! | 0.13667 | 0.12083 | #VALUE! | #VALUE! | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.11667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.083333 | 0.13667 | 0.13667 | 0.13667 | #VALUE! | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | 0.13667 | #VALUE! | 0.13667 | 0.13667 | 0.13667 | 0.13667